## Slide 1
Yokohama National University
* JSPS Research Fellow
ICHS2015
Jo Nakayama*, Junji Sakamoto, Naoya Kasai, Tadahiro Shibutani and Atsumi Miyake
Hazard identification study
for risk assessment on a hybrid gasoline-hydrogen fueling station with an onsite hydrogen production system using organic hydride
ID:173
Acknowledge
This study was supported by the “Promotion program for scientific fire and disaster prevention technologies” by the Fire and Disaster Management Agency (FDMA) of the Ministry of Internal Affairs and Communication in Japan.

## Slide 2
Introduction
1
In Japan,
Hydrogen fueling stations (HFSs)
In Germany,
400 stations by 2023
In Japan,
100 stations by 2015
In California,
87 stations by 2020
Planning to set “hydrogen town” as
athletes village for 2020 Olympic in Tokyo.
Accelerating station constructions and widely using FCVs.

## Slide 3
Classification of HFSs
2
 |  | Off-site |  | On-site | 
 |  | Compressed hydrogen | Liquefied hydrogen | LPG | Organic hydride (Methylcyclo-hexane (MCH))
Hydrogen fueling stations | Stand-alone | Hydrogen projects Risk analyses using qualitative and quantitative methods1-3) Laws, regulations and codes |  |  | No safety investigations
 | Hybrid H2-gasoline |  |  |  | 
Kikukawa, S., et al., International Journal of Hydrogen Energy, 34, 2009, pp. 1135-1141.
Kim, E., et al., International Journal of Hydrogen Energy, 38, 2013, pp. 1737-1743.
Nakayama, J., et al., Proceeding of GCPS2015, Austin, 2015.
Safety investigations
Risk assessment on a hybrid H2-gasoline fueling station with an on-site hydrogen production system using MCH can contribute to a “hydrogen society”.

## Slide 4
Research
Basic Design
Detailed Design
Construction
Operation
Conceptual
Design
Effectiveness of Hazard elimination or reduction2)
High
Low
ISO17776, Petroleum and natural gas industries –Offshore production installations– Guidelines on tools and techniques for hazard identification and risk assessment.
Srinivasan, R., and Natarajan, S., Process Safety and Environmental Protection, 90, 2012, pp. 389-403.
HAZID Study
FMEA, HAZOP, ETA, FTA
3
Risk assessment
  is a method of qualitative hazard analyses at an early stage in process lifecycle.
  helps to detailed risk analyses at later stages.
  can effectively eliminate or reduce hazards for inherent safety.
HAZID Study ≒ Preliminary Hazard Analysis (PHA)1)
Process Lifecycle
Purpose
HAZID Study for identification and evaluation of risks involving with MCH system in the hybrid station.

## Slide 5
4
Analysis procedure
Definition of the model of a hybrid H2-gasoline fueling station using on-site hydrogen production system with MCH
Introduction of HAZID Study method
HAZID Study for identification scenarios
Risk evaluation by risk matrix
Representative scenario identification
Comparative evaluation analysis of MCH and existing LPG-typed hydrogen fueling stations.
Conclusions

## Slide 6
A hybrid station model
5
MCH dehydrogenation
Gasoline
Hydrogen
82 MPa
< 1MPa
MCH

## Slide 7
A hybrid station model
5
MCH dehydrogenation
Gasoline
Hydrogen
82 MPa
< 1MPa
MCH
HAZID Study

## Slide 8
Introduction of HAZID Study
6
Hazard identification study (HAZID Study)
A qualitative accident scenario identification method
Scenarios are associated with GUIDEWORDs.
Guidewords
①Natural hazard (24 types)
ex. Earthquake, Tsunami, Typhoon
②External event hazard (15 types)
ex. Airplane crash, Terrorism, Automobile collision
③Station layout hazard (3 types)
ex. Evacuation
④Hybrid event hazard (6 types)
ex. Gasoline leakage, Fire fighting
⑤Process hazard (21 types)
ex. Combustible material, Explosion.
➡ specializing to detect hidden scenarios

## Slide 9
HAZID Study sheet
7
HAZID sheet consists of
① No.
② Guideword
③ Cause
④ Effect
⑤ Risk level without safety measures
（Consequence, Probability and Risk）
⑥ Current safety measures
⑦ Risk level with safety measures
⑧ additional actions
An example of HAZID sheet
Scenario description for risk evaluation

## Slide 10
HAZID study results
8
The hybrid station has 314 accident scenarios involving with MCH and gasoline systems.

## Slide 11
Risk matrix
 |  | Probability |  |  | 
 |  | 1 | 2 | 3 | 4
Consequence severity | 5 | 19 | 0 | 0 | 0
 | 4 | 95 | 27 | 0 | 0
 | 3 | 126 | 19 | 0 | 0
 | 2 | 26 | 2 | 0 | 0
 | 1 | 0 | 0 | 0 | 0
High Risk
Medium Risk
Low Risk
 |  | Probability |  |  | 
 |  | 1 | 2 | 3 | 4
Consequence severity | 5 | 0 | 71 | 98 | 0
 | 4 | 0 | 63 | 82 | 0
 | 3 | 0 | 0 | 0 | 0
 | 2 | 0 | 0 | 0 | 0
 | 1 | 0 | 0 | 0 | 0
Risk matrix without safety measures
Risk matrix with safety measures
Almost all risks are reduced by current safety measures.
46 risks remained as high regardless of operating safety measure.
9

## Slide 12
Representative common causes
Regardless of operating safety measures,
A gasoline car crashes into an operating MCH or toluene lorry.
A massive amount of gasoline is leaked and being spreading from an operating gasoline lorry for any reason. A gasoline pool fire affects the MCH system.
MCH or toluene disperses into the atmosphere while fire fighters are extinguishing a fire occurring at the MCH system.
New prevention and mitigation safety measures need to be added for risk reduction.
10
MCH system
Lorry position

## Slide 13
Suggestion of safety measures
11
For prevention of collision at lorry position, a collision guard is needed while a lorry are operating.
For prevention of spreading of gasoline pool around the lorry position, a water drain is needed to recover fuel.
For prevention and mitigation of escalation events while firefighting, a new tactics needs to be developed.
MCH or TOL dispersions
These additional measures can reduce risks.

## Slide 14
Comparative evaluation of MCH and LPG
12
MCH & TOL
LPG
 | MCH & TOL | LPG
Lorry | 2 times | 1 time
Storage tank | Under-ground | Over-ground
MCH or TOL is more likely to be leaked from faulty hose joints.
A BLEVE of MCH or TOL may be occurred at a lorry position.
LPG tank has a risk of a BLEVE.
Further analysis of incident involving MCH and TOL lorries.

## Slide 15
Conclusions
【Purpose】
HAZID Study for identification and evaluation of risks involving with MCH system in the hybrid station.
13
From the results of HAZID Study,
HAZID Study identified 314 accident scenarios.
3 unique scenarios were revealed, and additional safety measures were suggested.
The station was compared with a LPG-typed HFS, and remarkable points of the station were identified.
Future works
Detailed risk analysis of the MCH dehydrogenation system.
Quantitative hazard analysis of incident involving lorries.

## Slide 16
Thank you for your attention !