## Slide 1: Evaluation of Engineering Models for Vented Lean Hydrogen Deflagrations
Anubhav Sinha, Vendra Chandra and Jennifer X. Wen
Warwick FIRE, School of Engineering
University of Warwick, UK

## Slide 2: Outline
Introduction
Review of Engineering Models
Experimental studies
Performance Evaluation of Engineering Models
Effect of Obstacles
Predictions for New Experimental results
Concluding Remarks

## Slide 3: Introduction
Vented deflagrations – simplest way to relieve pressure
Experiments are expensive, specially for large enclosures / buildings
Computational models – challenge to incorporate large range of scales involved, time taking and large computational resources required
EM – reasonable predictions, simple and fast to use
Review Engineering models to assess their applicability for hydrogen deflagrations

## Slide 4: Review of Engineering Models
EN14994 (2007)1
NFPA 68 (2013) 2
Bauwens et al. (2012) 3
Molkov and Bragin (2015) 4
These models are reviewed and their applicability is tested with experimental results available in literature and from results generated in this project
[1] EN 14994 (2007). Gas explosion venting protective systems
[2] NFPA 68. (2013): Standard on explosion protection by deflagration venting, 2013 Edition, National Fire Protection Association, Quincy, MA 02269.
[3] Bauwens, C. R., Chao, J., & Dorofeev, S. B. (2012). Effect of hydrogen concentration on vented explosion overpressures from lean hydrogen–air deflagrations. International journal of hydrogen energy.
[4] Molkov, V., Bragin, M. (2015). Hydrogen–air deflagrations: Vent sizing correlation for low-strength equipment and buildings. International Journal of Hydrogen Energy, 40(2), 1256-1266.

## Slide 5: EN14994 (2007)1
The formulation is divided into two parts, one for a compact enclosure (with L/D≤2) and the other for elongated enclosure (with L/D>2)
A gas explosion constant KG which denotes maximum value of pressure rise per unit time is used to determine overpressure
The constant KG is determined experimentally
Effect of initial turbulence is not taken into account
Not recommended for Hydrogen

## Slide 6: NFPA 68(2013)2
This model consists of two formulations – one for low static pressure and another for high static pressure
Effect of turbulence on flame speed is accounted in this model formulation.
Different considerations are given to the vent deployment, whether it is a part of a wall or a complete side wall is used as a vent
In general, predictions from this model are conservative and tend to predict higher overpressures than experimentally obtained values

## Slide 7: Bauwens et al.3 Model
This model is based on the multi-peak behaviour of vented explosions due to various physical processes involved
Different formulations are give to derive maximum pressure for each peak
Three different pressure peaks considered are –
      External explosion (P1)
      Flame-Acoustic interaction (P2)
      Pressure peak due to presence of obstacles (P3)
The maximum value of all these peaks gives the final overpressure value

## Slide 8: Molkov and Bragin4 Model
This model is based on the novel concept of Deflagration-Outflow Interaction (DOI) number
The major assumption is that the overpressure correlates with the DOI number and can be related using the turbulent Bradley number
Various physical processes including initial turbulence, effect of elongated enclosure, effect of obstacles, fractal nature of flame-front, are accounted for in this model.
Two formulations are proposed – one for conservative estimate and other for best fit value

## Slide 9: Experimental Studies
These experimental studies are used to assess engineering models
[5] Kumar, K., Vented combustion of hydrogen-air mixtures in a large rectangular volume. In 44th AIAA Aerospace Sciences Meeting and Exhibit, 2006.
[6] Kumar, R. K. (2009). Vented Turbulent Combustion of Hydrogen-Air Mixtures in A Large Rectangular Volume. In 47th AIAA aerospace sciences meeting including the new horizons forum and aerospace exposition. Paper AIAA 2009-1380.
[7] Daubech, J., Proust, C., Jamois, D., Leprette, E. (2011, September). Dynamics of vented hydrogen-air deflagrations. In 4. International Conference on Hydrogen Safety (ICHS 2011)
[8] Schiavetti, M., and M. Carcassi. "Maximum overpressure vs. H 2 concentration non-monotonic behavior in vented deflagration. Experimental results." International Journal of Hydrogen Energy (2016).
5
6
7
3
8

## Slide 10
EN14994 Model (2007)1
Mixture composition is accounted for the factor KG (for compact enclosures)
For a given geometry and comparable fuel concentration, vent area is dominant factor
Data points are clustered as it gives similar prediction for fixed vent size
Predictions for Bauwens et al. (2012) experiments3
Predictions for Daubech et al. (2011) experiments7
Predictions for Kumar (2009) experiments6
Volume
Vent area
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Two cylindrical enclosures - 1 m3 and 10.5 m3
No obstacles
Line shows y = x
Cubical enclosure - 120 m3
No obstacles
Vent area

## Slide 11
Predictions for Bauwens et al. (2012) experiments3
Over-prediction for most data points (conservative estimate) for various experimental results
NFPA 68 Model (2013)2
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Predictions for Kumar (2006) experiments5
Predictions for Daubech et al. (2011) experiments7
Two cylindrical enclosure - 1 m3 and 10.5 m3
No obstacles
Cubical enclosure - 120 m3 – (L/D = 2.5)
No obstacles

## Slide 12
Predictions for Bauwens et al. (2012) experiments3
Predictions for Kumar’s experiments5,6
Predictions for Daubech et al. (2011) experiments7
Accounts for several physical aspects- calculates multiple peak pressures
Under-prediction for Kumar’s experiments – cases with high initial turbulence and high L/D (2.5)
Some experiments of Daubech et al. (2011) also show high over-prediction (L/D=3.3)
Bauwens et al. Model (2012)3
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Two cylindrical enclosure - 1 m3 and 10.5 m3
No obstacles
Cubical enclosure - 120 m3 – (L/D = 2.5)
No obstacles

## Slide 13
Predictions for Daubech et al. (2011) experiments7
Predictions for Bauwens et al. (2012) experiments3
Over-predicts for larger enclosure used by Daubech et al. (L/D=3.3) – for higher H2 concentrations
Bauwens et al. Model (2012)3
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Two cylindrical enclosures - 1 m3 (L/D = 1.4) and 10.5 m3 (L/D = 3.3)
No obstacles

## Slide 14
Predictions for Bauwens et al. (2012) experiments3
Predictions for Kumar (2009) experiments6
Ign location
Vent area
Predictions for Daubech et al. (2011) experiments7
In the formulation, two equations are suggested – conservative and best-fit
Best-fit formula appears to slightly under-predict for most of data points
Molkov and Bragin Model (2015)4
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Two cylindrical enclosures - 1 m3 and 10.5 m3
No obstacles
Cubical enclosure - 120 m3
No obstacles
Enclosure volume
For obstacles, Ξo is provided in Molkov and Bragin4 (3.5 for BW and 1.0 for CI)

## Slide 15
Predictions for Bauwens et al. (2012) experiments3
Predictions for Kumar (2009) experiments6
Predictions for Daubech et al. (2011) experiments7
The predictions appear to be reasonable for the experiments compared
The formulation of coefficient for obstacles is not clearly defined
Molkov and Bragin Model (2015)4
Cubical enclosure - 63.7 m3
Includes cases with obstacles
Two cylindrical enclosures - 1 m3 and 10.5 m3
No obstacles
Cubical enclosure - 120 m3
No obstacles
For obstacles, Ξo is provided in Molkov and Bragin4 (3.5 for BW and 1.0 for CI)

## Slide 16
Scarcity of data on systematic study of effect of obstacles
Schiavetti and Carcassi (2016) 8 – impact of obstacles in a small volume enclosure
Flat plates are used as obstacles
More such experiments required for realistic obstacles in a larger geometry
(Schiavetti and Carcassi (2016))8
Effect of Obstacles

## Slide 17
Obstacles – Molkov and Bragin Model (2015)4
Obs 3
Obs 2
Obs 4
Obs 6
Obs 5
Obs 8
Different values of Ξo used and plotted with various obstacle configurations
The best fit value of Ξo is shown in table
Obstacle config | Ξo (best fit)
Obs 2 | 2.00
Obs 3 | 2.00
Obs 4 | 2.00
Obs 5 | 2.00
Obs 6 | 3.00
Obs 8 | 3.50
(Schiavetti and Carcassi (2016))8

## Slide 18
Prediction for 20 feet ISO container
Bauwens et al. (2012) model3
Obs 1 – Bottle
Obs 2 – Pipe rack
Obs 3 – Bottle + Pipe rack
Venting through door
Venting through roof
Cubical enclosure – 33 m3
Includes cases with obstacles
Over-prediction is observed for cases with obstacles for both experimental sets

## Slide 19
Obs 1 – Bottle
Obs 2 – Pipe rack
Obs 3 – Bottle + Pipe rack
Cubical enclosure – 33 m3
Includes cases with obstacles
Venting through door
Prediction for 20 feet ISO container
Molkov and Bragin (2015) model4
Ξo = 1.25
Ξo = 2.0
Ξo = 3.5
Using Ξo = 3.5 – (recommended for obstacles in FM global tests) 4 gives over-prediction
Blockage Ratio | Ξo | Experiments
0.06 | 3.50 | Bauwens et al. (2012) - BW ignition
0.30 | 1.25 | GexCon 20 ft ISO container-bottles – BW
0.12 | 1.25 | GexCon 20 ft ISO container -pipe and rack- BW

## Slide 20
Both NFPA 68 and EN 14994 models over-predicted the experimental measurements
The predictions of Bauwens et al. (2012) model and Molkov and Bragin (2015) model (without obstacles) are in reasonable agreement with the experimental data, but both models have some limitations:
  The predictions of Bauwens et al. (2012) model have relatively large discrepancy for high L/D enclosures and cases with high initial turbulence
  Molkov and Bragin (2015) model does not provide any specific treatment for obstacles. Instead obstacles can only be considered through adjusting the coefficient Ξo
  Neither considers stratified distribution of the fuel
Non-monotonous behaviour observed near H2 concentration of 10% (Kumar-2006 and Schiavetti and Carcassi -2016). This is not captured by any of the models.
Concluding remarks

## Slide 21
Thank
You